Independent University, Bangladesh

Study on Grid and Substation Operation & Maintenance of DESCO

An undergraduate internship report submitted by

Navila Rahman (Student ID: 0820109)

in consideration of the partial fulfillment of the requirements for the degree of

BACHELOR OF SCIENCE

in

ELECTRICAL AND ELECTRONIC ENGINEERING

Department of Electrical and Electronic Engineering

Spring 2010

Study on Grid and Substation Operation

& Maintenance of DESCO

An undergraduate internship report submitted by

Navila Rahman (Student ID: 0820109)

has been approved on December 15, 2010.

______________________________

Dr. M. Abdur Razzak

Internship Supervisor & Associate Professor

Department of Electrical and Electronic Engineering

School of Engineering & Computer Science

Independent University, Bangladesh

ACKNOWLEDGEMENTS

All praises go to Allah, the almighty, for the successful completion of this internship and fulfillment of author’s dream into reality. However, thanks and gratitude are also due to the following persons for their continuous support in completing this internship and in preparing this report.

First of all, the author would like to express his sincere appreciation, heartfelt gratitude and cordial thanks to her internship supervisor, Dr. M. Abdur Razzak, Associate Professor, Department of Electrical and Electronic Engineering, Independent University, Bangladesh, for his invaluable instructions, continuous guidance, constructive criticisms and thoughtful advice during pursuing this internship and preparation of this report.

Next, the author is grateful to Engr. Monjurul Haque, DGM of DESCO for his vast support for this internship.

Special thanks are extended to the author’s fellow classmates of the Department of Electrical and Electronic Engineering, Independent University, Bangladesh for their helping hand, continuous support and cooperation during this internship.

Finally, the author proudfully acknowledges the great sacrifices, good wishes, moral support, fruitful advice, inspirations and encouragements from her family members, relatives and friends which help the author to finish the internship successfully.

The Author

December 2010

Dhaka, Bangladesh

ABSTRACT

Electricity plays a vital role in the socio-economic development and poverty alleviation. It is considered as the driving force of all development activities. To alleviate poverty in the face of resource limitations and high population density, Bangladesh requires an economic growth rate of about 10% p.a. to provide employment to its rapidly growing labor force that cannot be absorbed by agriculture. In order to achieve this growth rate, availability of a reasonably priced and reliable source of electricity is a prerequisite.

The power sector in Bangladesh faced numerous problems characterized by lack of supply capacity, frequent power cuts, unacceptable quality of supply, and poor financial and operational performance of the sector entities. The customer service is not praiseworthy. There have been a number of reforms in the power sector in Bangladesh since her independence, but most of these reforms failed to bring desired improvements in the power sector. The most pressing problem in the power sector has been with the distribution system, which is characterized by heavy system loss and poor collection performance; however, the distribution system seldom got the priority in reform initiatives.

In the process of Power Sector Reforms by way of unbundling the power sector and increase efficiency in the area of electricity distribution, Dhaka Electric Supply Company Limited (DESCO) was created as a distribution company in November 1996 under the Companies Act 1994 as a Public Limited Company with an Authorized Capital of Tk. 5 billion. However the operational activities of DESCO at the field level commenced on September 24, 1998.The primary aims in creating DESCO were to provide better consumer service and to improve revenue collection.

In this internship report, the daily operation of DESCO, their electricity distribution & metering system as well as the substation equipment and switchgear & protective devices are studied.

TABLE OF CONTENTS

Acknowledgement									iii

Abstract										iv

List of Figures										viii

List of Tables										ix

Chapter 1 	Introduction

  - Background							1

## Objective							2

## Scope of the Study						2

## Research Methodology						3

    - Nature of the Study					3

    - Data Collection						4

      - Primary Source				5

      - Secondary Source				6

## Limitations of the Study						7

Chapter 2 	Company Profile

- Dhaka Electric Supply Company Ltd.				8

- Major Works Involved						9

- Territory								9

- Supply Chain							10

- Mission and Vision						11

- Operation							12

- Departments of DESCO						13

- Some Other Utility Service Provider in Bangladesh 		14

Chapter 3 	Literature Review

- Introduction							15

- How Electrical Distribution Works				16

- Power System							17

    - Generation System					17

    - Transmission System					18

    - Distribution System					19

- Important Terms of Power System				20

    - Transformer						20

    - Substation						21

    - Power Factor						22

    - Electricity Consumer					23

    - Demand Load						24

    - Installed Capacity					25

    - Electric Energy Measuring Unit			26

    - System Loss						27

Chapter 4	Grid and Substation Operation

- Grid								28

- Substation							29

- Description of the Components and Their Operation		30

    - Power Transformer					30

      - Transformer Principal				31

      - Grid Transformer				32

      - Substation Transformer			33

      - Oil Type Transformer				34

    - Circuit Breaker						35

      - SF6 Circuit Breaker				35

      - Vacuum Circuit Breaker			36

    - Current Transformer					37

    - Potential Transformer					38

    - Isolator							39

    - Lightning Arrestor					40

    - Bus Bar							41

    - Auxiliary Transformer					42

    - AC and DC Distribution Panel				42

    - Control Relay Panel					43

- Protection of Power System					44

- Transformer protection Scheme					45

- Transformer Fault and Protection				46

        - Buchholz Relay						46

        - Differential Relay					47

        - Pressure Relief Relay					48

        - Over Current and Earth Fault Protection		49

- Feeder Protection Schemes					50

          - O/C and E/F Protection in Feeder			50

          - Pilot Wire Protection					52

- Bus bar Protection 						53

Chapter 5	Summary and Future work

- Summary							54

- Future work							55

References 									56

Appendices

Appendix A								59

Appendix B								60

Appendix C								61

LIST OF FIGURES

Figure								          Page

2.1	Operation of Sales & Distribution division					11

3.1	Typical alternating current power supply scheme				18

4.1	Grid and substation operation							30

4.2	Typical substation								31

4.3	Single line diagram of 132/33KV Bashundhara grid substation		32

4.4	Single line diagram of 33/11KV Baridhara substation 			33

4.5	Components of power transformer						34

4.6	SF6 circuit breaker								36

4.6	Name plate of SF6 circuit breaker						37

4.7	Name plate of vacuum circuit breaker					38

4.8	Current transformer of Bashundhara grid					39

4.9	Potential transformer of Bashundhara grid					40

4.10	Disconnecting switch								41

4.11	Lightning arrestors								42

4.12	Lightning arrestor of Bashundhara Grid					42

4.13	Reserve bus bar system							44

4.14	Bus bar system in Bashundhara Grid						46

4.15	Control relay panel								49

LIST OF TABLES

Table								          Page

2.1 	General information of DESCO						8

2.2	Commercial and system operational function of DESCO			10

4.1 	General Equipments of Grid and Substation					30